## Slide 1: CHAPTER 3 Well posed predictive control 5 Changing the input horizons
Anthony Rossiter

## Slide 2: Introduction
The previous videos demonstrated, through examples and simple argument, that the use of an input horizon of 2 was an improvement on the use of 1, for most cases.
Similar conclusions arose with nu=1 or 2, that is in general with low output horizons, the optimisation does not reflect enough of the predicted behaviour to be meaningful.
With high output horizons, the steady-state error dominates J and thus the final value goes directly to the steady-state, which in essence means only one of the degrees of freedom is available for optimisation.
For systems with undesirable open-loop dynamics (such as open-loop unstable processes), nu=2 gives insufficient flexibility within the predicted control trajectory to form desirable predictions.
This video overlays plots with several different nu simultaneously in an effort to gain insight into a systematic proposal for horizon choices.

## Slide 3: Aside - feedforward
So far these videos are assuming there is no advance information on the target, so in essence the feedforward Pr is a constant and the target is assumed constant.
Discussions on how ‘tuning’ guidance might change when advance information on the target is available is delayed until later so as not to confuse core concepts.
However, viewers should note that there is a very strong link between nu and behaviour when feedforward is provided.

## Slide 4: gpc3_5_example1, ny=5
Low ny, predictions are poor for all choices of nu!
An optimisation based on ny=5 cannot be trusted to give good overall strategy.

## Slide 5: gpc3_5_example1, ny=15
As nu increases, the predictions get closer to what could be considered a good overall strategy.
Although the outputs are fairly fixed for nu>=3, there are some subtle changes in the proposed input trajectory – BUT, NOT the 1st value!

## Slide 6: Open-loop prediction vs closed-loop
With high ny and high nu the actual closed-loop behaviour is very similar to the open-loop prediction within the horizon (and beyond).
This suggests the optimisation is well-posed.
Good closed-loop behaviour is more likely to be due to good design.

## Slide 7: gpc3_5_example2, ny=5
In this case, increasing nu is making things worse.
Of course this is because ny is too small because the system is NMP.

## Slide 8: gpc3_5_example2, ny=20
For large ny, we find nu>=2 is enough to get reasonable predictions, but the larger nu, the better!
Again, input predictions, especially the 1st value, become fairly steady for nu>=3.

## Slide 9: Open-loop prediction vs closed-loop
With high ny and high nu the actual closed-loop behaviour is very similar to the open-loop prediction within the horizon (and beyond).
This suggests the optimisation is well-posed.
Good closed-loop behaviour is more likely to be due to good design.

## Slide 10: gpc3_5_example3, ny=5
Predictions within the horizon improve with increasing nu, but overall predictions still very poor (divergent).
A low ny is dangerous as we do not observe the long term risks.

## Slide 11: gpc3_5_example3, ny=15
Increasing ny gives us more confidence in the transient predictions, but the divergent tail is till worrying.
Input predictions, especially the 1st value, become fairly steady for nu>=2.

## Slide 12: Open-loop prediction vs closed-loop
With high enough ny and high nu the actual closed-loop behaviour is very similar to the open-loop prediction within the horizon (feedback saves us from the divergence beyond).
This suggests the optimisation is well-posed.
Good closed-loop behaviour is more likely to be due to good design.

## Slide 13: gpc3_5_example 4 with ny=5
Complex poles, but stable.
Increasing nu has helped but only a little impact here because ny is too small to observe and overcome the unpleasant open-loop dynamics.

## Slide 14: gpc3_5_example 4 with ny=15
Complex poles, but stable.
Increasing nu now has a good impact because ny is large enough to observe and compensate for open-loop dynamics.
Need nu>=4!
Input predictions settle for nu>=4.

## Slide 15: Open-loop prediction vs closed-loop
With high enough ny and high nu the actual closed-loop behaviour is very similar to the open-loop prediction within the horizon (and beyond).
This suggests the optimisation is well-posed.
Good closed-loop behaviour is more likely to be due to good design.

## Slide 16: Observation summary for nu
Use of low output horizons, even with large nu rarely gives rise to sensible predictions. The optimisations results from such a scenario cannot usually be trusted and so should be avoided.
Long output horizons in combination with larger input horizons allow better predicted performance and in most cases shown, indicated good performance both within the horizon window and beyond which is a main indicator of a well posed optimisation. (The exception is open-loop unstable processes)
For the examples shown, the differences in the first input value were minimal for nu equal to around 3 or greater. The suggestion therefore is that there is rarely a need for nu to be very large, although of course some cases may require nu =10 or more. It is easy to do trial and error to check.
These videos have not yet considered the impact of changing the weights on the input – this is needed before we make any final conclusions.

## Slide 17
© 2014 University of Sheffield
This work is licensed under the Creative Commons Attribution 2.0 UK: England & Wales Licence. To view a copy of this licence, visit http://creativecommons.org/licenses/by/2.0/uk/ or send a letter to: Creative Commons, 171 Second Street, Suite 300, San Francisco, California 94105, USA.
It should be noted that some of the materials contained within this resource are subject to third party rights and any copyright notices must remain with these materials in the event of reuse or repurposing.
If there are third party images within the resource please do not remove or alter any of the copyright notices or website details shown below the image.
(Please list details of the third party rights contained within this work.
If you include your institutions logo on the cover please include reference to the fact that it is a trade mark and all copyright in that image is reserved.)
Anthony Rossiter
Department of Automatic Control and Systems Engineering
University of Sheffield
www.shef.ac.uk/acse